# eDIN #1004 Demultiplexer Module  Specifications

# Version 2.0

July 2013

# SUBJECT TO CHANGE WITHOUT NOTICE

1.0	General

1.1	The eDIN Demultiplexer Module shall provide digital to analog conversion of DMX512 input to 0-10VDC (nominal) output.

1.2	Each module shall provide sixteen (16) channels of analog output, with each output controlled by a discrete DMX channel. The starting DMX channel shall be user-selectable.

1.3	Minimum and maximum output voltages shall be user-selectable within a range of 0 to 16 volts DC at up to 10mA per output (sourcing) and 30mA per output (sinking).

1.4	Each output shall be provided with a blocking diode and a shunt switch to allow the user to bypass the diode to suit the application.

1.5	The Module shall be designed to mount on 35mm DIN rail.

2.0	Features

2.1	The module shall have 7 user-selectable operating modes, including but not limited to:

2.1.1 	0-10 volts DC output range.

2.1.2	0-5 volts DC output range.

2.1.3 	0-15 volts DC output range.

2.1.4	0-2.5 volts DC output range.

2.1.5	Custom output range. The user shall be able to set a minimum voltage output to correspond with a DMX input level of 0%, and a maximum voltage output to correspond to a DMX input level of 100%. Minimum voltage output shall range from 0 to 15.5 volts DC. Maximum voltage output shall range from 0 to 16 volts DC.

2.1.6	8 channel electronic fluorescent ballast / LED driver controller. This mode shall provide control of up to eight circuits of 0-10V devices, with a maximum of 50 ballasts/drivers on each circuit.  Outputs shall be paired (1 with 9, 2 with 10, etc). The lower output shall provide 0 to 10 volts DC intensity control to the devices. The upper output shall provide on/off control to a solid state relay switching the circuit’s AC power feed. The solid state relay shall open or close as the DMX value passes through the low-end control threshold.

(NOTE:  This module provides a control interface only. For a complete panel solution incorporating power relays, contact Pathway Connectivity.)

2.1.7	Non-Dim mode. This mode shall provide 16 current-sinking outputs. When DMX levels are 0%, output voltage shall be as configured by the max level setting. When DMX levels pass through 50% increasing, output levels shall fall to 0 volts DC. The mode shall require the blocking diodes are shunted (by-passed). (NOTE: Module power supply must be 12VDC for this mode.)

2.2	A dry contact closure input shall be provided as a panic override. When the input is shorted (closed), all outputs shall be forced to full-on, regardless of DMX input values.

2.3	The Module shall have a diagnostic test mode, activated by pressing a pushbutton during power-up.

2.4	The Module shall provide an output test mode to allow the user to activate a selected analog output via the onboard user interface.

3.0	User Interface

3.1	A three-digit LED display and three pushbuttons shall provide the user interface to set DMX start address, operating mode, minimum and maximum voltage outputs as required and to access test functions.

3.2	LEDs shall be provided to indicate status for power, isolated power, processor status and DMX input.

3.3 	The Module shall also be discoverable and configurable via a remote controller using RDM.

3.4	A DMX end-of-line termination switch shall be provided on the Module.

4.0 	Electrical

4.1	Multiple modules, up to the RS485 limitation of 32, may be daisy-chained on the same DMX input data line.

4.2	The power input shall be supplied by a Class 2 circuit. It shall accept a range of 9 to 30 volts DC and shall consume no more than 6 watts.

4.3	The DMX input port shall be capable of withstanding short-term application of up to 250V without damage to internal components.

4.4	DMX input protection shall be self-healing, rated for 250V. Replaceable fuses shall not be acceptable.

4.5	The DMX input port shall provide 1500-volt optical isolation between the DMX input signal and analog output signals.

4.6	Each analog output shall be rated for a maximum 16 volts DC and maximum current of 10 mA (sourcing) or 30 mA (current sinking).

4.7	The Module shall be equipped with a blocking diode for each output to prevent accidental damage to the module when used in current sinking applications.  It shall be possible for the user to by-pass the diodes on an output-by-output basis via shunt switches, to allow use in current sourcing applications or where the blocking diodes are not needed.

4.8	All DMX, output and power connections shall utilize pluggable Phoenix-type screw terminal blocks, capable of accepting solid or stranded wire sizes from #26 to #16 AWG.

5.0	Protocol Compatibility

5.1	The input control signal shall be compatible with all variants of the lighting industry standard DMX512 control protocol. The output signal shall be compatible with industry standards for 0-10V analog control.

5.2	One (1) DMX Pass-Thru port shall be provided. The Pass-Thru port shall be passive, that is, direct-wired from the input and not repeated, such that failure of the Module shall not adversely affect a signal being passed through to another module or device.

5.3	The Demultiplexer Module shall support RDM (Remote Device Management) for discovery and configuration.

5.4	It shall be possible to update the module’s firmware via the DMX port. Products that provide no firmware update capability will not be acceptable.

6.0	Physical

6.1	The Demultiplexer Module shall be designed to snap on to 35mm DIN rail without the use of tools.

6.2	The Module shall measure 3.6”W x 6.25”L x 1.50”H (91mm x  160mm x 38mm).

6.3	The Module shall weigh 0.53 lb. (240g).

7.0	Environmental

7.1	The ambient operating temperature shall be -10° to 50°C (14° to 122°F).

7.2	The storage temperature shall be -40° to 70°C (-40° to 158°F).

7.3	The operating humidity shall be 5% - 95% non-condensing.

8.0	Compliance

8.1	The DMX Demultiplexer Module shall meet the requirements of USITT DMX512 (1990), ANSI E1.11 DMX512-A, and ANSI E1.20 Remote Device Management.

8.2	Analog outputs shall meet the requirements of ANSI E1.3 0-10V Analog Control when the shunt switches are closed, and ANSI C82.11 when the shunt switches are open.

8.3	The DMX Demultiplexer Module shall be compliant with the EU RoHS (2002/95/EC) directive.

8.4	The DMX Demultiplexer Module shall conform to all FCC and CE requirements.

8.5	The DMX Demultiplexer Module shall be powered by a UL1310 Class 2 Low Voltage circuit.

8.6	The module circuit board shall be manufactured from FR-4 glass epoxy laminate with a UL 94 flammability rating of V0. The board shall be clearly marked as such.

8.7	The module carrier housing shall be manufactured from extruded rigid PVC with a UL 94 flammability rating of 5VA.

9.0	Acceptable Product

9.1	The DMX Demultiplexer Module(s) shall be Pathway Connectivity eDIN model #1004.