# eDIN #1008 LED Dimmer / DC Driver  Specifications

# Version 2.1

July 2013

# SUBJECT TO CHANGE WITHOUT NOTICE

1.0	General

1.1	The eDIN LED Dimmer / DC Driver Module shall be a multi-purpose LED dimming controller and solid state DC driver. It shall convert DMX512 input signals to high current switched or pulse-width modulated DC output drives.

1.2	The Module shall be capable of driving constant-voltage LED fixtures and other low-voltage DC loads.

1.3	The Module shall provide six outputs, each operated by a discrete DMX channel (two discrete channels in high resolution mode). The starting DMX channel shall be user-selectable.

1.4	Each output shall provide dimming control from 0% to 100% for one circuit of LED fixtures up to a maximum load of 96W @ 24VDC (48W @ 12VDC) per output.

1.5	The Module shall be designed to mount on 35mm DIN rail.

2.0	Features

2.1	The Module shall have several user-selectable operating modes, including but not limited to the following:

2.1.1	Standard 6-channel LED Dimming mode. The module shall translate six DMX 8-bit signals to 16-bit control by means of a high-resolution software fade algorithm to ensure even, step-free fading of LED intensity.  8-bit fade resolution shall be unacceptable. The linear DMX control signal shall be translated to an LED-specific output curve so that, to the human eye, the LEDs appear to fade linearly from zero to full. Straight linear outputs shall not be acceptable.

2.1.2	3-channel LED Dimming mode. Same as above, but with three pairs of outputs controlled by 3 DMX channels.

2.1.3	1-channel LED Dimming mode. Same as above, but with all six outputs controlled by one DMX channel.

2.1.4	Double Precision Control with Fade Curve. Each output shall be controlled by two sequential DMX channels to produce a true16-bit value for calculating intensity. The linear DMX control signal shall be translated to an LED-specific output curve so that, to the human eye, the LEDs appear to fade linearly from zero to full. Straight linear outputs shall not be acceptable.

2.1.5	Double Precision Control without Fade Curve. Each output shall be controlled by two sequential DMX channels to produce a true 16-bit value for calculating intensity. The linear DMX control signals shall determine the output PWM values in a straight linear fashion, without use of any curve to compensate for human eye response.

2.1.6	Non-Dim Control. This mode shall switch, not dim, the outputs. When the DMX value for an output is below 50%, the output shall be off (open). When the DMX value is above 50%, the output shall be on (closed). This mode shall efficiently drive solenoid coils or solid state relays.

2.2	Six (6) discrete 0-10V analog inputs shall be provided. These inputs operate in a highest-takes-precedence mode with the DMX input values.

2.3	One (1) dry contact closure input shall be provided as a panic override. When the input is shorted (closed) to signal common, all outputs shall be forced to full, regardless of DMX input values.

2.4	The Module shall include one (1) Form-C relay output which shall function as a DMX-present detector.

2.5	The Module shall have a diagnostic mode, activated by pressing a pushbutton during power-up.

2.6	The Module shall provide an output test mode to allow the user to activate a selected output via the onboard user interface.

3.0	User Interface

3.1	A three-digit LED display and three pushbuttons shall provide the user-interface to set DMX start address, operating mode, minimum and maximum output level and to access test functions.

3.2	LED indicators shall provide status reporting for power input, isolated DMX power, processor OK, DMX input, and output mimic.

3.3 	The Module shall also be discoverable and configurable via a remote controller using RDM.

3.4	A DMX end-of-line termination switch shall be provided on the Module.

4.0	Electrical

4.1	Multiple modules, up to the RS485 limitation of 32, may be daisy-chained on the same DMX input data line.

4.2	The power input shall be supplied by a Class 2 circuit. It shall accept a range of 9 to 30 volts DC and shall consume no more than 5 watts.

4.3	The DMX input port shall be capable of withstanding short-duration application of up to 250V without damage to internal components.

4.4	DMX input protection shall be self-healing, rated for 250V. Replaceable fuses shall not be acceptable.

4.5	The input port shall provide 1500-volt optical isolation between the DMX signal and module electronics.

4.6	The Module shall be capable of driving any constant-voltage LED fixture rated at between 5 to 30 volts DC. LED fixtures of differing voltage ratings may be driven by the same module.

4.7	Each output shall be capable of driving connected loads up to four (4) amperes at 24VDC.

4.8	Each output shall be fuse-protected and fully electrically isolated to 2500V from all other outputs to eliminate the possibility of system malfunction or damage due to accidental grounding or other electrical faults. Two spare socketed fuses shall be provided on each module.

4.9	DMX connections, DC output and power connections shall all utilize pluggable Phoenix-type screw terminal blocks, capable of accepting solid or stranded wire sizes from #26 to #14 AWG.

5.0	Protocol Compatibility

5.1	The DMX input shall be compatible with all variants of the lighting industry standard DMX512 protocol.

5.2	One (1) DMX Pass-Thru port shall be provided. The Pass-Thru port shall be passive, that is, direct-wired from the input and not repeated, such that failure of the Module shall not adversely affect a signal being passed through to another module or device.

5.3	The LED Dimmer / DC Driver Module shall support RDM (Remote Device Management) for discovery and configuration.

5.4	It shall be possible to update the module’s firmware via the DMX port. Products that provide no firmware update capability will not be acceptable.

6.0	Physical

6.1	The LED Dimmer/DC Driver module shall be designed to snap on to 35mm DIN rail, without the use of tools.

6.2	The Module shall measure 3.6”W x  8”0L x 1.5”H (91mm x  200mm x 38mm).

6.3	The Module shall weigh 0.7 lb. (315g).

7.0	Environmental

7.1	The ambient operating temperature shall be -10° to 50°C (14° to 122°F).

7.2	The storage temperature shall be -40° to 70°C (-40° to 158°F).

7.3	The operating humidity shall be 5% - 95% non-condensing.

8.0	Compliance

8.1	The LED Dimmer / DC Driver Module shall meet the requirements of USITT DMX512 (1990), ANSI E1.11 DMX512-A, and ANSI E1.20 Remote Device Management.

8.2	Analog inputs shall meet the requirements of ANSI E1.3 0-10V Analog Control.

8.3	The LED Dimmer / DC Driver Module shall be compliant with the EU RoHS (2002/95/EC) directive.

8.4	The LED Dimmer / DC Driver Module shall conform to all FCC and CE requirements.

8.5	The LED Dimmer / DC Driver Module shall be powered by a UL1310 Class 2 Low Voltage circuit.

8.6	LED power circuits shall conform to UL1310 Class 2.

8.7	The module circuit board shall be manufactured from FR-4 glass epoxy laminate with a UL 94 flammability rating of V0. The board shall be clearly marked as such.

8.8	The module carrier housing shall be manufactured from extruded rigid PVC with a UL 94 flammability rating of 5VA.

9.0	Acceptable Product

9.1	The LED Dimmer / DC Driver Module(s) shall be Pathway Connectivity eDIN model #1008.