# eDIN #1009 DMX/RDM Repeater Module  Specifications

# Version 2.1

July 2013

# SUBJECT TO CHANGE WITHOUT NOTICE

1.0	General

1.1	The eDIN DMX/RDM Repeater Module shall permit star-wiring and repeating of DMX512 and RDM lighting control signals over the connected data cabling.

1.2	The Module shall fully isolate and protect DMX transmitters and receivers, and RDM controllers and responders from high common mode voltages, ground loop currents and other potentially damaging or disrupting electrical faults.

1.3	The Module shall have one input port, one pass-thru port and four output ports. All ports shall be bi-directional.

1.4	There shall be no in-line processing of the input signal, to ensure that all output signals are exact duplicates of the input signal with no processing delays.

1.5	The Module shall be capable of repeating and distributing simplex protocols other than DMX512, provided they meet the electrical requirements of EIA-RS422 or RS485.

1.6	The Module shall be designed to mount on standard 35mm DIN rail.

2.0	Features

2.1	LED indicators shall be provided for Power, Data-In and CPU status, as well as for DMX/RDM activity on each of the four output ports.

2.2	The Module shall be capable of regenerating four (4) exact duplicate data streams from the original source input data stream.

2.3	Each output shall be capable of driving up to 32 DMX-only receiving devices over a maximum 500-meter (1600-ft.) length of cable.

2.4	Each output shall be capable of driving up to 31 DMX/RDM responding devices over a maximum 300-meter (1000-ft.) length of cable.

2.5	One (1) DMX/RDM pass-thru port shall be provided. The pass-thru port shall be active, i.e. electrically repeated.

2.6	For installations requiring DMX and RDM functionality, up to four repeater modules may be cascaded together. For installations requiring only DMX functionality, up to eight repeater modules may be cascaded together.

2.7	The Module itself shall act as an RDM responder.

2.8	It shall be possible to field-update the module firmware via the DMX input port.

3.0 	Electrical

3.1	The power input shall be supplied by a Class 2 circuit. It shall accept a range of 9 to 30 volts DC and shall consume no more than 6 watts.

3.2	Multiple modules, up to the RDM-specified limitation of four (4), may be cascaded (looped) on the same DMX/RDM input data line using the pass-thru ports or any output ports.

3.3	In DMX-only installations, up to eight (8) modules may be cascaded (looped) on the same DMX input data line using the pass-thru ports or any output ports.

3.4	All DMX/RDM input and output ports shall be capable of withstanding short-term application of up to 250V without damage to internal components.

3.5	Port protection shall be self-healing, rated for 250V. Replaceable fuses shall not be acceptable.

3.6	The DMX/RDM input port shall provide 1500-volt optical isolation between the input signal wiring and output signal wiring.

3.7	DMX/RDM output ports shall be fully optically isolated from each other and floating with respect to earth ground.

4.0	Physical

4.1	The DMX/RDM Repeater module shall be designed to snap on to 35mm DIN rail without the use of tools.

4.2	The Module shall measure 3.6”W x 6.25”L x 1.5”H (91mm x  160mm x 38mm).

4.3	The Module shall weigh 0.54 lb. (245g).

4.4	All DMX and power connections shall utilize pluggable Phoenix-type screw terminal blocks, capable of accepting solid or stranded wire sizes from #26 to #16 AWG.

5.0	Environmental

5.1	The ambient operating temperature shall be -10° to 50°C (14° to 122°F).

5.2	The storage temperature shall be -40° to 70°C (-40° to 158°F).

5.3	The operating humidity shall be 5% - 95% non-condensing.

6.0	Compliance

6.1	The DMX/RDM Repeater Module shall meet the requirements of USITT DMX512 (1990), ANSI E1.11 DMX512-A and ANSI E1.20 RDM.

6.2	The DMX/RDM Repeater Module shall be compliant with the EU RoHS (2002/95/EC) directive.

6.3	The DMX/RDM Repeater Module shall conform to all FCC and CE requirements.

6.4	The DMX/RDM Repeater Module shall be powered by a UL1310 Class 2 Low Voltage circuit.

6.5	The module circuit board shall be manufactured from FR-4 glass epoxy laminate with a UL 94 flammability rating of V0. The board shall be clearly marked as such.

6.6	The module carrier housing shall be manufactured from extruded rigid PVC with a UL 94 flammability rating of 5VA.

7.0	Acceptable Product

7.1	The DMX/RDM Repeater Module(s) shall be Pathway eDIN model #1009.